## DYKEDIME
Containment Program For Small Lateral Aperatures |  |  |  | Engineering Formulas, Page N7
Case: | Demonstration Example |  | Calc dyke dimensions to contain any leak location.
|  |  | Dyke L = | 146.7218
144.9521
Chemical | Toluene
Tonnes Liq = | 4356.9078 |  | S | Dia | S
Liq Dens = | 54.4 | lb/cf | 22.476 | 100 | 22.476
Tank Diam = | 100 | Ft. |  | Ht = | 30
Tank Height = | 30 | Ft. | 7.5188
Hole Height = | 11 | Ft. above grade, h |  |  | H Ab Hole = | 11.4812
Liquid Head = | 22.4812 | Ft. above grade | 22.4812 |  | Hole Ht, h = | 11
Ht Ab Hole = | 11.4812 | Ft. (H) |  |  |  | 22.4812
Dist S, ft. = | 22.476 | 2((H)(h))^0.5
Tank Vol = | 235619.449 | cu.ft | slope | S | S = | 22.476
Tons Liq = | 4802.6195
Cu Ft. Liq = | 176566.8923 | cf | 5000 | cu.m. | To recovery storage
% Full = | 74.94%
Dyke Area = | 2000 | m2 L x L = | 44.7214 | meters | 146.7218 | ft
Tank Area = | 729.6765 | m2
Pool Area = | 1270.3235 | m2 for spill area evaporation.
Pool Ht = | 2.5 | meters | 8.202 | ft | 98.424 | inches
Dyke Height = | 5 | meters | 16.404 | ft. | 196.848 | inches
Dyke L x L = | 146.7218 | ft. based on square dimensions and vertical, concrete walls.
Req'd L = | 144.9521 | ft. to retain leak within dyke
Message = | Req'd L < Dyke L and Leak Should Stay Within Dyke
Dutch Guide Basis: |  | Class F2 for Flammable Liquids
Tank With Dyke |  | 2500 | m2 recommended by Dutch Guide.
| Vol, m3 |  | Spill Area, m2
| < 3000 |  | 1500
| 3000 - 10,000 |  | V/2
| > 10,000 |  | V/2.5 to Max 10,000
Processing Plant
| Vol, m3 |  | Spill Area, m2
| <0.05 |  | 10
| 0.05 - 1 |  | 50
| 1 - 10 |  | 250
| > 10 |  | 1500
If actual dyke area is known, enter it as the pool area.
Note on B16: Basis: Page N7, Hydraulics